## Tags
TagID | Tag | Process | Location Detail | Units | Tag (Units) | Purpose | Notes
86 | Ozone Production Error | Ozone |  | decimal | Ozone Production Error (decimal) | Value
67 | Ozone Normalized Difference (Across Meters) OSP 4 | Ozone | OSP 4 | decimal | Ozone Normalized Difference (Across Meters) OSP 4 (decimal) | Value
59 | Ozone Demand Hach Meter | Ozone | Hach | mg/L | Ozone Demand Hach Meter (mg/L) | Value
21 | Ozone LRV via Cryptosporidium | Ozone |  | LRV | Ozone LRV via Cryptosporidium (LRV) | Value
10 | MF Filtrate Turbidity | MF | Filtrate | NTU | MF Filtrate Turbidity (NTU) | Value
15 | RO Combined Permeate TOC | RO | Combined Permeate | ug/L | RO Combined Permeate TOC (ug/L) | Value
29 | RO Train A Permeate Conductivity | RO | Train A Permeate | uS/cm | RO Train A Permeate Conductivity (uS/cm) | Value
31 | RO Train B Permeate Conductivity | RO | Train B Permeate | uS/cm | RO Train B Permeate Conductivity (uS/cm) | Value
1 | RO Feed TOC | RO | Feed | mg/L | RO Feed TOC (mg/L) | Value
17 | RO LRV via TOC | RO |  | LRV | RO LRV via TOC (LRV) | Value
40 | UV Dose | UVAOP |  | mJ/cm2 | UV Dose (mJ/cm2) | Value
65 | UV Intensity | UVAOP |  | mW/cm2 | UV Intensity (mW/cm2) | Value
32 | UV Feed UVT | UVAOP | Feed | % | UV Feed UVT (%) | Value
83 | RO Permeate Total Chlorine | UVAOP | Permeate | mg/L | RO Permeate Total Chlorine (mg/L) | Value
48 | BAC Filter 1 Status | Ozone | Filter 1 |  | BAC Filter 1 Status | Status | 1 = production. BAC filter status indicates ozone status
49 | BAC Filter 2 Status | Ozone | Filter 2 |  | BAC Filter 2 Status | Status | 1 = production. BAC filter status indicates ozone status
64 | MF Status | MF |  |  | MF Status | Status | 1 = production
43 | Plantwide Status | All |  |  | Plantwide Status | Status | 1 = production
91 | Ozone Normalized Difference (Inst vs Rolling) OSP 4 Hach | Ozone | OSP 4 Hach | decimal | Ozone Normalized Difference (Inst vs Rolling) OSP 4 Hach (decimal) | Value
92 | Ozone Normalized Difference (Inst vs Rolling) OSP 7 Hach | Ozone | OSP 7 Hach | decimal | Ozone Normalized Difference (Inst vs Rolling) OSP 7 Hach (decimal) | Value
58 | Ozone Demand Rosemount | Ozone | Rosemount | mg/L | Ozone Demand Rosemount (mg/L) | Value
68 | Ozone Normalized Difference (Across Meters) OSP 7 | Ozone | OSP 7 | decimal | Ozone Normalized Difference (Across Meters) OSP 7 (decimal) | Value

## Events
EventID | Event Text | Event Process | Event Type | TagIDs
1 | High Filtrate Turbidity (0.15 NTU) | MF | Process | 10
2 | Stagnant Filtrate Turbidimeter | MF | Monitoring | 10
3 | Not applicable | MF | Water Quality 1
4 | Not applicable | MF | Water Quality 2
5 | Potential Membrane Breach | RO | Process | 15, 29, 31
6 | Feed TOC Meter Drift | RO | Monitoring | 1, 17
7 | Chemical Peak | RO | Water Quality 1 | 15, 29, 31
8 | Not applicable | RO | Water Quality 2
9 | Low UV Dose | UVAOP | Process | 40
10 | Stagnant UV Intensity Sensor | UVAOP | Monitoring | 65
11 | Low UV Feed UVT | UVAOP | Water Quality 1 | 32
12 | High UV Feed Chloramines | UVAOP | Water Quality 2 | 83
13 | Partial Ozone Generator Failure | Ozone | Process | 86
14 | Meter Drift at Ozone Meter | Ozone | Monitoring | 67, 68
15 | High Ozone Demand | Ozone | Water Quality 1 | 91, 86, 59
16 | Not applicable | Ozone | Water Quality 2

## Outlier Tests (hidden)
TestID | TagID | TagIDLong | Tag Description | Units | Test Description | Lower Bound (stdev) | Upper Bound (stdev) | Minimum Failure Duration (mins) | Test Frequency | Moving Window Size | Action | Test Order
Outlier_1 | #REF! | #REF! | RO Feed TOC | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_2 | #REF! | #REF! | RO Combined Permeate TOC | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_3 | #REF! | #REF! | RO EC Removal | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_4 | #REF! | #REF! | RO TOC Removal | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_5 | #REF! | #REF! | RO Cryptosporidium LRV | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_6 | #REF! | #REF! | RO Giardia LRV | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_7 | #REF! | #REF! | RO Virus LRV | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_8 | #REF! | #REF! | RO Feed Conductivity | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_9 | #REF! | #REF! | RO Train A Permeate Conductivity | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_10 | #REF! | #REF! | RO Train B Permeate Conductivity | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_11 | #REF! | #REF! | RO Feed TOC | #REF! | Chronic outlier | -1 | 1 | 1440 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_12 | #REF! | #REF! | RO Combined Permeate TOC | #REF! | Chronic outlier | -1 | 1 | 1440 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_13 | #REF! | #REF! | RO EC Removal | #REF! | Chronic outlier | -1 | 1 | 1440 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_14 | #REF! | #REF! | RO TOC Removal | #REF! | Chronic outlier | -1 | 1 | 1440 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_15 | #REF! | #REF! | RO Cryptosporidium LRV | #REF! | Chronic outlier | -1 | 1 | 1440 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_16 | #REF! | #REF! | RO Giardia LRV | #REF! | Chronic outlier | -1 | 1 | 1440 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_17 | #REF! | #REF! | RO Virus LRV | #REF! | Chronic outlier | -1 | 1 | 1440 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_18 | #REF! | #REF! | RO Feed Conductivity | #REF! | Chronic outlier | -1 | 1 | 1440 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_19 | #REF! | #REF! | RO Train A Permeate Conductivity | #REF! | Chronic outlier | -1 | 1 | 1440 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_20 | #REF! | #REF! | RO Train B Permeate Conductivity | #REF! | Chronic outlier | -1 | 1 | 1440 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_21 | #REF! | #REF! | OSP 4 Meter | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
Outlier_22 | #REF! | #REF! | OSP 7 Meter | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
Outlier_23 | #REF! | #REF! | OSP 10 Meter | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
Outlier_24 | #REF! | #REF! | OSP 4 Meter 2 | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
Outlier_25 | #REF! | #REF! | OSP 7 Meter 2 | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
Outlier_26 | #REF! | #REF! | Ozone Generator Production Rate | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_27 | #REF! | #REF! | Water flow | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_28 | #REF! | #REF! | Calculated ozone decay between locations 1 and 2 | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
Outlier_29 | #REF! | #REF! | Calculated ozone decay between locations 1 and 3 | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
Outlier_30 | #REF! | #REF! | Ozone Cryptosporidium LRV | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
Outlier_31 | #REF! | #REF! | Ozone Giardia LRV | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
Outlier_32 | #REF! | #REF! | Ozone Virus LRV | #REF! | Acute outlier | -2 | 2 | 2 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
| #REF! | #REF! | MF Filtrate Turbidity | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
| #REF! | #REF! | UF Filtrate Turbidity | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
| #REF! | #REF! | Tertiary Effluent TOC | #REF! | Acute outlier | -2 | 2 | 10 | Every 1 minute | Daily | Flag, Keep, and Alert | 2
| #REF! | #REF! | Applied Ozone Dose | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
| #REF! | #REF! | Ozone Demand 1 | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
| #REF! | #REF! | Ozone Demand 2 | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
| #REF! | #REF! | Expected OSP 7 Reading 1 | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
| #REF! | #REF! | Expected OSP 7 Reading 2 | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
| #REF! | #REF! | Ozone to TOC ratio | #REF! | Acute outlier | -2 | 2 | 10 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
| #REF! | #REF! | UF Temperature | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Every 15 minutes | Flag, Keep, and Alert | 2
| #REF! | #REF! | UV Ballast Power | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Daily | Flag, Keep, and Alert | 1
| #REF! | #REF! | MF/UF Feed Chloramines | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Daily | Flag, Keep, and Alert | 1
| #REF! | #REF! | UV Influent Sodium Hypochlorite Pump Speed | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Daily | Flag, Keep, and Alert | 1
| #REF! | #REF! | UV Intensity Sensor | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Daily | Flag, Keep, and Alert | 1
| #REF! | #REF! | Cumulative Train Cryptosporidium LRV | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Daily | Flag, Keep, and Alert | 1
| #REF! | #REF! | Cumulative Train Giardia LRV | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Daily | Flag, Keep, and Alert | 1
| #REF! | #REF! | Cumulative Train virus LRV | #REF! | Acute outlier | -2 | 2 | 5 | Every 1 minute | Daily | Flag, Keep, and Alert | 1